{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Predizmere"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Predizmere","index":0,"n_rows":137,"n_cols":3,"rows_kept":137,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["VN OMREŽJE TER TP - gradbena dela"]
[]
["1. Gradbena dela"]
[]
["1.1. KbV 20 kV Obrtna cona Ajdovščina II – Obrtna cona Ajdovščina III"]
[]
["1.  Zakoličba trase kabelske kanalizacije","m",310]
[]
["2.  Zakoličba lokacije jaškov","kos",6]
[]
["3.  Zakoličba obstoječih komunalnih naprav"]
["     ( vodovod, kanalizacija, plinovod,…)","kos",5]
[]
["4.  Izkop jarka za kabelsko kanalizacijo"]
["      0,6 x 1,0 m v terenu 3. ktg","m",310]
[]
["5.  Izdelava posteljice za kabelske cevi z peskom"]
["     granulacije 0-4 mm, debeline 10 cm","m",300]
[]
["6.  Polaganje kabelskih cevi stigmaflex EZ 3 x 110"]
["     na peščeno blazino","m",300]
[]
["7.  Polaganje kabelskih cevi stigmaflex "]
["     EZ 3 x 110 in obbetoniranje z betonom MB 15","m",10]
[]
["8.  Zasipanje položenih kabelskih cevi z peskom"]
["     granulacije 0-4 mm, debeline 10 cm","m",300]
[]
["9.  Zasipanje jarka z izkopanim materialom, nabijanje "]
["     v plasteh in urejanje poškodovanih površin"]
["     po končanih delih","m",150]
[]
["10. Zasipanje jarka z tamponom, nabijanje "]
["      v plasteh in urejanje poškodovanih površin"]
["      po končanih delih","m",150]
[]
["11. Betoniranje vrhnje plasti z betonom MB 15"]
["      po voznih površinah ( pod plastjo asfalta )","m",10]
[]
["12. Polaganje ozemljitvenega valjanca"]
["      FeZn 25 x 4 mm ( po celotni trasi )","m",310]
[]
["13. Polaganje opozorilnega traku z napisom "]
["      »POZOR ELEKTRIKA« ( po celotni trasi )","m",310]
[]
["14. Izkop jame dimenzij 2,5 x 2,5 x 1,4 m za kabelski"]
["      jašek 1,5 x 1,5 x 1,0 m ( svetle mere ) v terenu 3. ktg do 4.ktg,"]
["      odvoz odvečnega materiala na primerno deponijo"]
["      ( oddaljeno do 5 km ), zasip in urejanje "]
["      poškodovanih površin po končanih delih","kos",3]
[]
["15. Izdelava kabelskega jaška dimenzij 1,5 x 1,5 x 1,0 m"]
["      ( svetle mere ) ter z dvojnim litoželeznim"]
["      pokrovom 60 x 60 cm, nosilnosti 250 kN"]
["      napisom »ELEKTRIKA«","kos",3]
[]
["16. Izkop jame dimenzij 3,0 x 2,5 x 1,4 m za kabelski"]
["      jašek 2,0 x 1,5 x 1,0 m ( svetle mere ) v terenu 3. ktg do 4.ktg,"]
["      odvoz odvečnega materiala na primerno deponijo"]
["      ( oddaljeno do 5 km ), zasip in urejanje "]
["      poškodovanih površin po končanih delih","kos",1]
[]
["17. Izdelava kabelskega jaška dimenzij 2,0 x 1,5 x 1,0 m"]
["      ( svetle mere ) ter z dvojnim litoželeznim"]
["      pokrovom 60 x 60 cm, nosilnosti 250 kN"]
["      napisom »ELEKTRIKA«","kos",1]
[]
["18. Izkop jame dimenzij 2,5 x 2,0 x 1,4 m za kabelski"]
["      jašek 1,5 x 1,0 x 1,0 m ( svetle mere ) v terenu 3. ktg do 4.ktg,"]
["      odvoz odvečnega materiala na primerno deponijo"]
["      ( oddaljeno do 5 km ), zasip in urejanje "]
["      poškodovanih površin po končanih delih","kos",1]
[]
["19. Izdelava kabelskega jaška dimenzij 1,5 x 1,0 x 1,0 m"]
["      ( svetle mere ) ter z dvojnim litoželeznim"]
["      pokrovom 60 x 60 cm, nosilnosti 250 kN"]
["      napisom »ELEKTRIKA«","kos",1]
[]
["20. Izkop jame dimenzij 2,5 x 2,2 x 1,4 m za kabelski"]
["      jašek 1,5 x 1,2 x 1,0 m ( svetle mere ) v terenu 3. ktg do 4.ktg,"]
["      odvoz odvečnega materiala na primerno deponijo"]
["      ( oddaljeno do 5 km ), zasip in urejanje "]
["      poškodovanih površin po končanih delih","kos",1]
[]
["21. Izdelava kabelskega jaška dimenzij 1,2 x 1,2 x 1,0 m"]
["      ( svetle mere ) ter z enojnim litoželeznim"]
["      pokrovom 60 x 60 cm, nosilnosti 250 kN"]
["      napisom »ELEKTRIKA«","kos",1]
[]
["22. Odvoz odvečnega materiala na ustrezno "]
["      deponijo ( oddaljeno do 5 km )","m3",170]
[]
["23. Stroški zavarovanja gradbišča","kpl",1]
[]
["24. Stroški nadzora","h",8]
[]
["SKUPAJ"]
[]
[]
["1.2. TP 20/0,4 kV Obrtna cona Ajdovščina III"]
[]
["1.  Zakoličba lokacije in gabaritov TP","kos",1]
[]
["2.  Izkop jame dimenzij 7,00 x 6,00 x 1,00 m "]
["     v terenu 3. ktg za tipsko montažno transformatorsko"]
["     postajo tipa IMP 4, odvoz odvečnega materiala"]
["     na primerno deponijo ( oddaljeno do 5 km ), zasip in urejanje "]
["     poškodovanih površin po končanih delih","kos",1]
[]
["3.  Izdelava podložnega betona debeline 10 cm"]
["     za temeljni podstavek ( korito ) TP","m2",22]
[]
["4.  Izkop jarka za ozemljitev 0,4 x 0,6 m v "]
["     terenu 3. ktg , zasip in urejanje"]
["     poškodovanih površin po končanih delih","m",40]
[]
["5.  Polaganje ozemljitvenega valjanca"]
["     FeZn 25 x 4 mm "]
["     ( dva ozemljilna obroča okoli TP + 2 x 20 m )","m",95]
[]
["6.  Montažni predfabricirani betonski del "]
["     transformatorske postaje tipa IMP 4"]
["     ( vključno z AL vrati in žaluzijami )","kos",1]
[]
["7.  Zasipanje okolice TP z tamponom,"]
["     nabijanje v plasteh in urejanje poškodovanih "]
["     površin po končanih delih","m",20]
[]
["8.  Izdelava pločnika okoli TP iz  "]
["     pranih plošč 40 x 40 cm ( spredaj širine dve plošči,"]
["     ostale strani širine ene plošče )","m2",11]
[]
["9.  Stroški zavarovanja gradbišča","kpl",1]
[]
["10. Stroški nadzora","h",4]
[]
["SKUPAJ"]